# Methods

Draft for the thesis chapter. Numbers are taken from the model output in results/ (code version on main, ERA5 year 2023). Parameter values and their sources are listed in full in Table T1 (results/paper/tables/T1_parameters.md).

## 1 Study design

The study models the electric power system of a generic oil platform in the northern North Sea (Tampen area, 61.0° N, 2.0° E) for one year at hourly resolution. Power is supplied by gas turbines (GTs) and, in the wind cases, by a nearby offshore wind farm. The novelty compared with earlier platform–wind studies is that the topside demand is not treated as a fixed load: each consumer is mapped to its process duty and classified by how far, and at what cost, it can be moved in time or reduced. An optimisation model then schedules the flexible consumers together with the GTs.

Four cases are compared:

- Gas turbines only (baseline), fixed demand.

- Wind + GTs, fixed demand: production and water injection at their design and target rates every hour.

- Wind + GTs, flexible scheduling: production and water-injection rates are decision variables.

- Case 3 + battery (4 MW / 4 MWh).

In all cases the platform keeps its three existing GTs (a retrofit, as on the Snorre and Gullfaks platforms supplied by Hywind Tampen); the optimiser decides how many run in each hour. Process behaviour is represented by steady-state operating points with ramp limits; transient process dynamics are outside the scope.

The model is written in Python. NeqSim is used for thermodynamics and process simulation, Pyomo with the HiGHS solver for optimisation. Every parameter is stored in one configuration file with its unit and source, and unverified values are explicitly marked as assumptions (29 of 101 parameters). The code has a test suite of 49 automated checks that compare model components with hand calculations and published values.

## 2 Wind resource and wind farm power

Hourly wind components at 100 m for 2023 were taken from the ERA5 reanalysis (Hersbach et al., 2020) at the grid point 61.0° N, 2.0° E. Wind speed was extrapolated to the 150 m hub height with the power law

vhub=v100zhubz100α,  α=0.11,

the value recommended for near-neutral conditions at sea (Hsu et al., 1994). Turbine power was interpolated on the power curve of the IEA 15 MW offshore reference turbine (Gaertner et al., 2020): cut-in 3 m/s, rated power from 10.7 m/s, cut-out 25 m/s. The base-case farm has two turbines (30 MW installed), of the same order as the 32 MW wind farm of the LEOGO reference platform (Svendsen et al., 2023). Wake losses (5 %), electrical losses (2 %) and availability (95 %) reduce the delivered power by a combined factor of 0.884, so the farm delivers at most 26.5 MW.

## 3 Gas turbines, fuel gas and CO2

The GTs follow the LEOGO reference turbine (Svendsen et al., 2023): rated electric power 21.8 MW, minimum stable load 3.5 MW (16 %), three units installed. Fuel use is linear in electric output (a Willans line):

Qfuel=Pratedηrateda u+1−aPPrated,

where u is 1 when the unit runs, ηrated=0.347 and the no-load fuel fraction a=0.184 follow from the LEOGO fuel coefficients (A=2.35, B=0.53; ηrated=1/A+B, a=B/A+B). Efficiency therefore falls from 34.7 % at full load to 29.3 % at half load and 17.7 % at minimum load, and the specific CO2 emission rises from 623 to 737 and 1,220 kg/MWh. Half of the heat in the exhaust that is not converted to electricity is recovered as useful heat.

The lower heating value of the fuel gas, 38.96 MJ/Sm3, was computed with NeqSim according to ISO 6976 from a generic North Sea fuel-gas composition. CO2 emissions use the Norwegian standard factor of 2.34 kg CO2 per Sm3 fuel gas (Statistics Norway, as used in LEOGO). A carbon balance of the assumed composition gives 2.27 kg/Sm3, and reported Gullfaks data give 2.32–2.40 kg/Sm3 (Section 8), which supports the value used.

## 4 Topside process model and power per consumer

The process was modelled in NeqSim with the Peng–Robinson equation of state for hydrocarbons and the CPA equation of state for water, which reproduces liquid-water density and therefore pump power (SRK overestimated water-pump power by about 30 % in a test). The flowsheet is:

- four-stage separation at 70 / 29.2 / 7.9 / 1.8 bara (Voldsund et al., 2013, and related North Sea platform studies);

- three recompression stages lifting gas from each separator to the next stage, each followed by a cooler (30 °C) and a scrubber;

- gas export compression to 180 bara (isentropic efficiency 0.75);

- oil export pumping to 50 bara (pump efficiency 0.60);

- water injection pumps from 7 to 250 bara (efficiency 0.75);

- seawater lift pumps supplying cooling water (10 K temperature rise) and make-up water for injection (10.4 bar lift);

- a fixed utility load of 3.5 MW and a heat demand of 3 MW.

Pressures, efficiencies and loads not referenced otherwise are from LEOGO. The design point is 15,000 Sm3/d oil, a gas–oil ratio of 179 Sm3/Sm3 (2.68 MSm3/d gas export), a water cut of 40 % (10,000 m3/d produced water) and 25,000 m3/d water injection. The resulting electric demand at design is 20.3 MW (Table 1).

Table 1. Electric power at the design point.

| Consumer | Power [MW] | Share |
| --- | --- | --- |
| Water injection pumps | 9.19 | 45 % |
| Gas export compression | 3.73 | 18 % |
| Utilities and base load | 3.50 | 17 % |
| Recompression | 1.95 | 10 % |
| Oil export pumps | 1.48 | 7 % |
| Seawater lift pumps | 0.44 | 2 % |
| Total | 20.29 |  |

At fixed pressures and efficiencies, steady-state power is proportional to flow. Part-load behaviour was therefore represented by equipment limits: each consumer has a number of identical parallel trains, which can be switched off at low flow, and a minimum flow per train below which the train recycles (anti-surge recycle for compressors, minimum-flow recirculation for pumps). Gas export compression has 2 × 50 % trains, recompression one train, oil export pumps 2 × 50 %, water injection and seawater lift pumps 3 × 33 %. The minimum flow is 70 % for compressors and 30 % for pumps (assumed).

## 5 Consumer classification and flexibility

Each consumer was assigned to one class and one operating lever:

- Must-run: utilities and base load (3.5 MW), never reduced.

- Flexible (deferrable): water injection pumps. The lever is the injection rate fwi (fraction of pump capacity). Postponed injection is not lost but must be caught up.

- Sheddable: recompression, gas export compression and oil export pumps. The lever is the production rate fp; any reduction is lost production.

- Mixed: seawater lift pumps (cooling part follows fp, make-up part follows fwi).

The power of each lever group is a piecewise-linear function of the lever, derived from the trains and minimum flows of Section 4. For production it rises from 3.97 MW at 50 % rate to 4.72 MW just above 50 % (the second export compressor train starts at its surge limit), 5.01 MW at 70 % and 7.16 MW at 100 %. For injection it is 0 when all pumps are stopped, 0.92 MW with one pump on minimum-flow recycle (up to 10 % rate) and rises linearly to 9.19 MW at full rate.

Production can be turned down to 50 % and changed by at most 10 % of design per hour. Injection can vary between 0 and 100 % of pump capacity, by at most 34 % per hour (about one pump started or stopped). Its average must equal a voidage-replacement target of 85 % of capacity. This is modelled as a virtual storage: postponing injection builds a deficit D, measured in hours of full-rate injection,

Dt=Dt−1+fwitarget−fwi,t Δt,  0≤Dt≤Dmax=72 h.

The deficit limit represents how much injection the reservoir tolerates being postponed and is treated as an uncertain assumption; it is varied from 0 to 168 h in the sensitivity analysis.

## 6 Scheduling model

The schedule is found with a mixed-integer linear program solved hourly over the year. Decision variables are fp, fwi, the on/off state and power of each GT, wind power used (the rest is curtailed), electric-heater power and, in case 4, battery charge and discharge. The constraints are:

- power balance: GT power + wind used + battery discharge − charge = platform demand + electric heater;

- heat balance: recovered GT exhaust heat + electric heater (efficiency 0.99) ≥ 3 MW heat demand;

- GT limits: minimum and rated load when running, the Willans fuel line, start-up indicators;

- spinning reserve: unused capacity of running GTs plus battery reserve ≥ 5 MW (LEOGO); a battery counts only if it can sustain the reserve for 30 min;

- at least one GT online, because the wind turbines are grid-following and a GT is needed for frequency and voltage control (assumption, varied in the sensitivity analysis);

- the lever curves, ramp limits and injection deficit of Section 5, and the battery energy balance (round-trip efficiency 0.9).

The objective minimises, in NOK, the value of fuel gas burned (gas price 4.19 NOK/Sm3, since fuel gas could otherwise be exported), the CO2 cost (2.0 NOK/kg, the Norwegian target for the total CO2 price in 2030), the value of lost oil and gas (4,190 NOK/Sm3 oil) and a start-up cost of 2,000 NOK per GT start (prices from LEOGO). Unserved energy and missing reserve are allowed only with a penalty of 10⁶ NOK/MWh to keep the problem feasible; in all reported runs they are zero apart from numerical rounding (< 0.03 MWh/yr).

The year is solved as 52 rolling windows of one week, each optimised with a 24 h look-ahead that is not committed. At the end of each window horizon the injection deficit may not exceed, and the battery energy may not fall below, their values at the window start. The solver stops within 0.5 % of the proven optimum. One case-year takes about 2–3 minutes on a laptop-class CPU.

Because fuel is linear in power, the split of load between identical running GTs does not change fuel use, and the solver’s split is arbitrary. GT load is therefore reported as shared in proportion to rating (droop sharing, as in real operation), and an hour counts as a low-load hour when this shared load is below 50 % of rating.

## 7 Sensitivity analysis

Cases 2–4 were re-run with one input changed at a time: wind farm size (1–4 turbines, 15–60 MW), CO2 price (0.5–3.0 NOK/kg), gas price (2–8 NOK/Sm3), battery size (0–8 MW, 0–16 MWh), injection deficit limit (0–168 h), minimum number of GTs online (1 or 0, with an 8 MW / 8 MWh battery), GT fleet (three 21.8 MW units, or two plus one smaller 19 MW unit with unverified data) and an operating practice that keeps two GTs online regardless of wind.

## 8 Validation

Model results were compared with independent published values and field data:

- Platform power against measured and modelled North Sea platforms (Voldsund et al., 2013; Nguyen et al., 2013), the Johan Castberg plan for development and operation, and the average demand implied by Hywind Tampen (384 GWh/yr covering about 35 % of five platforms’ electricity).

- Wind capacity factor against Hywind Tampen (expected 384 GWh/yr from 88 MW; 58.4 % in Q1 2025).

- CO2 avoided per MWh of wind against Hywind Tampen (about 200 kt/yr for 384 GWh/yr, 0.52 t/MWh).

- Water-injection specific energy against LEOGO.

- CO2 intensity against the Norwegian shelf average for 2023 (7.3 kg/boe, Offshore Norge, 2024) and non-electrified hubs (about 10.5 kg/boe, Westwood, 2022).

- Field data for the Gullfaks, Snorre and Statfjord field centres for 2021, 2023 and 2024: CO2 to air, fuel gas and diesel use from the Norwegian Environment Agency (Norskeutslipp), and net production from the Norwegian Offshore Directorate (Sodir FactPages), summed over the fields processed at each centre. The boundary was checked by comparing oil volumes; they agree within 2 %.

A single published value counts as agreeing when the model is within ±20 %; a published range when the model lies inside it.

## 9 Main limitations of the method

- Generic platform: fluid composition, minimum-flow limits, injection target and deficit limit are assumptions (Table T1).

- Steady-state process; no transient compressor or reservoir response.

- Perfect foresight of wind within each week (no forecast error).

- The model includes only power generation; flaring, diesel use and gas re-injection, which add to real field emissions, are outside the boundary.

- One weather year (2023).

## 10 Comparison site: deepwater gas off southern Tanzania

To test whether the result depends on the North Sea setting, the same model is applied to a second, contrasting site. Only what differs is set in a separate configuration (config/tanzania.yaml), which inherits every other parameter from the base case; the same code, wind turbine, gas turbines, scheduler and cases are used.

Site and weather. The site is the deepwater gas discoveries in Blocks 1, 2 and 4 off Lindi and Mtwara (9.5° S, 40.5° E, water depth 1000–3000 m), the resource behind the planned Tanzania LNG project. Wind, 2 m air temperature and sea-surface temperature for 2023 come from ERA5, processed as in Section 2. The two IEA 15 MW turbines are assumed to sit on floating foundations, as at Hywind Tampen; the power curve is unchanged.

Platform and process. The platform is a hypothetical gas processing platform that sends 10 MSm³/d of dry gas (about a quarter of a two-train LNG plant) through a 100 km, 0.6 m pipeline to shore. The real development concept is subsea wells tied back to an onshore plant, so the platform is a modelling device that makes the two sites comparable, not a description of the project. A lean gas (95.5 mol % methane) arrives at 70 bara and 15 °C. NeqSim (Peng–Robinson) models the inlet separation, condensate stabilisation at 10 bara, and compression of the gas to 150 bara for export, with the same isentropic efficiency as the North Sea compressors. Gas dehydration with triethylene glycol (TEG) and regeneration of the mono-ethylene glycol (MEG) injected into the subsea wells for hydrate control are represented by their heat and electric duties (Table T1). These duties were checked against NeqSim water contents of the gas. Drying 10 MSm³/d needs a TEG reboiler of about 0.5 MW. Regenerating the MEG that carries the water condensed between reservoir and platform needs about 1 MW of heat, for an assumed reservoir of 80 °C and 300 bara. The MEG injection pumps need only about 0.05 MW (docs/verification/tanzania_process_check.py). The design electric demand is 15.4 MW, of which export compression is 11.2 MW (73 %).

Flexibility levers. A gas platform has no water injection, so the two levers are different:

- Gas production and line pack. The export pipeline stores gas. Allowing its inlet pressure to swing between 150 and 110 bara stores 3.6 h of full-rate production, computed from NeqSim gas densities at the two pressures and the pipeline volume. The platform may produce between 50 % and 110 % of the sales rate, as long as the deficit against the sales rate never exceeds the line pack and is repaid by the end of the horizon. Delivered gas, and therefore the LNG plant, is unaffected on average; no production is lost.

- MEG regeneration. Rich MEG is buffered in a tank, so the regeneration unit (0.1 MW electric and 1 MW heat at full rate) may pause for up to 48 h of full-rate feed and catch up later, exactly as water injection is modelled for the North Sea platform. The MEG injection pumps are must-run.

The TEG and MEG heat duties follow the two levers, so the heat balance of Section 6 changes with the schedule.

Hot climate. Gas turbine power and efficiency are derated for the ERA5 mean air temperature (26.8 °C, 11.8 K above ISO conditions) by 0.7 %/K and 0.1 %/K, rule-of-thumb values that should be replaced by a manufacturer’s site rating. The LEOGO turbine then delivers 20.0 MW at 34.3 % efficiency. Coolers use the ERA5 mean sea temperature (28.2 °C).

Fuel and CO2 price. The fuel is the lean export gas. Its lower heating value (34.9 MJ/Sm³) is computed with NeqSim to ISO 6976, and its CO2 factor (1.945 kg/Sm³) from its carbon content, instead of the Norwegian 2.34 kg/Sm³. The base CO2 price is the excise duty introduced by the Tanzanian Finance Act 2025: TZS 22,000 per tonne of carbon emissions from coal and natural gas, about NOK 0.09/kg at 10.5 NOK/USD. Whether it applies to fuel gas burnt offshore is not confirmed. CO2 prices of 0–2 NOK/kg are therefore tested as a sensitivity, together with line-pack sizes of 0, 1.8, 3.6 and 7.2 h.

Validation. No published operating data exist for an offshore platform at the site. The wind input is checked qualitatively against a study of measured winds at coastal Tanzanian stations, which reports the strongest winds at Mtwara and a June–July maximum with weak winds from November to March, and against the ESMAP offshore-wind potential maps. Of the 115 parameters in the Tanzania configuration, 43 are still assumptions, 22 of them specific to Tanzania (Table T1; docs/verification/tanzania_assumptions.md).

## References

Gaertner, E. et al. (2020). Definition of the IEA 15-Megawatt Offshore Reference Wind Turbine. NREL/TP-5000-75698.

Hersbach, H. et al. (2020). The ERA5 global reanalysis. Quarterly Journal of the Royal Meteorological Society 146, 1999–2049.

Hsu, S. A., Meindl, E. A. & Gilhousen, D. B. (1994). Determining the power-law wind-profile exponent under near-neutral stability conditions at sea. Journal of Applied Meteorology 33, 757–765.

Nguyen, T.-V. et al. (2013). Exergetic assessment of energy systems on North Sea oil and gas platforms. Energy.

Offshore Norge (2024). Climate and environmental report 2024.

Sharqawy, M. H., Lienhard, J. H. & Zubair, S. M. (2010). Thermophysical properties of seawater. Desalination and Water Treatment 16, 354–380.

Svendsen, H. G. et al. (2023). The Low Emission Oil and Gas Open reference platform – an off-grid energy system for renewable integration studies. IET Energy Systems Integration. doi:10.1049/esi2.12085.

Voldsund, M., Ertesvåg, I. S., He, W. & Kjelstrup, S. (2013). Exergy analysis of the oil and gas processing on a North Sea oil platform a real production day. Energy 55, 716–727.

Westwood Global Energy (2022). Analysis of electrification and emissions on the Norwegian continental shelf.

ESMAP (2020). Offshore Wind Technical Potential: Analysis and Maps. World Bank Energy Sector Management Assistance Program. https://www.esmap.org/esmap_offshorewind_techpotential_analysis_maps

Wind patterns of coastal Tanzania (University of Dar es Salaam repository). https://repository.udsm.ac.tz/items/2f0fb49f-1275-4710-b7f1-116e2bdf0264 (authors and year to be completed from the original).

Data: Copernicus Climate Change Service (ERA5); Norwegian Environment Agency, Norskeutslipp (CompanyID 22311, 16791, 16790); Norwegian Offshore Directorate, FactPages (field production, yearly).

Check before submission: references marked “verify” in docs/parameter_verification.md were obtained from search summaries and should be confirmed against the original documents.